AGIRE / WATERWISE PROJECT

Integrated water resource management — Nam Sa basin

Bolikhamxay Province, Lao PDR

~~

TECHNICAL SPECIFICATIONS

Geophysical investigation and construction of water supply boreholes

Stage 1 — desk study, electrical resistivity survey and siting | Stage 2 — drilling, well completion, development, pumping tests and reporting

| Item | Reference |
| --- | --- |
| Client | Comité de Coopération avec le Laos (CCL) |
| Site supervision | AGIRE project team — Paksan provincial office |
| Institutional partners | Provincial Health Office (PHO) Bolikhamxay; Nam Saat (DHO Paksan); PONRE / DWR |
| Funding partners | AFD, City of Paris, Fondation Groupe EDF, Rhin-Meuse Water Agency |
| Subject | Services and works contract — geophysical siting study and borehole drilling campaign |
| Procedure | Restricted consultation — minimum three candidates |
| Tender reference | AGIRE/TRV/2026/01X |
| Deadline for offers | 18th September 2026, 17:00 Vientiane time |
| Version — date | v1.0 (EN) 28th August 2026 |

# Table of contents

Table of contents	2

1. Background, scope and contract structure	4

1.1 Project background	4

1.2 Two-stage structure and decision gate	4

1.3 Scope of services	4

1.4 Exclusions	5

1.5 Contract structure and cost control	5

1.6 Contract documents	6

2. Target villages and design duty	6

2.1 Villages, population and location	6

2.2 Purpose of the standby borehole	6

2.3 Design duty of the boreholes	6

3. Stage 1 — Geophysical investigation and siting	7

3.1 Desk review — no site visit	7

3.2 Geophysical survey	7

3.3 Targeting report	8

3.4 Siting criteria	9

3.5 Joint site confirmation	9

3.6 Decision gate	10

4. Obligations prior to commencement	10

4.1 Unexploded ordnance — chance find procedure	10

4.2 Permits and authorisations	10

4.3 Land access and community information	11

5. Technical specifications for the boreholes	11

5.1 Drilling method and equipment	11

5.2 Depths and diameters	11

5.3 Target aquifer and isolation of the shallow aquifer	12

5.4 Sampling and drilling records	13

5.5 Casing, screens and gravel pack	13

5.6 Sanitary annular grouting	13

5.7 Development	14

5.8 Disinfection	14

6. Pumping tests and acceptance	14

6.1 General	14

6.2 Step-drawdown test	14

6.3 Constant-rate test	15

6.4 Interpretation	15

6.5 Acceptance criteria	15

6.6 Unproductive boreholes — the Contractor's replacement obligation	16

6.7 Plugging and abandonment	16

7. Water quality	16

8. Securing the wellhead	17

8.1 Wellhead — mandatory	17

8.2 Concrete apron — optional	17

8.3 Securing the site pending equipment	18

9. Health, safety, environment and social requirements	18

9.1 Safety of personnel and third parties	18

9.2 Management of sludge, cuttings and drilling fluid	19

9.3 Hydrocarbons, waste and nuisance	19

9.4 Social and integrity requirements	19

10. Deliverables	20

11. Programme and site organisation	21

11.1 Indicative programme	21

11.2 Supervision and staffing	21

12. Supervision, hold points and acceptance	21

12.1 Hold points	21

12.2 Provisional and final acceptance	22

13. Contractual and financial provisions	22

13.1 Form of prices	22

13.2 Payment	22

13.3 Liquidated damages and remedies	22

13.4 Subcontracting and variations	23

14. Content of offers and evaluation	23

14.1 Composition of the offer	23

14.2 Evaluation criteria	23

Annex A — Bill of quantities	25

Annex B — Borehole summary sheet template	27

Annex C — Typical borehole design	28

C.1 Summary of mandatory requirements	28

C.2 Typical borehole design	29

# 1. Background, scope and contract structure

## 1.1 Project background

The AGIRE project, also referred to as WaterWise, is implemented by the Comité de Coopération avec le Laos (CCL) in the Nam Sa catchment, a tributary of the Mekong located in Bolikhamxay Province (Paksan and Pakkading districts) in close partnership with the Bolikhamxay Provincial Health Department. The project works in ten villages representing approximately 7,800 people, around three objectives: access to safe drinking water, local governance of water resources, and sustainable management of the environment.

The water access assessment carried out in February 2026 established that the villages covered by this contract lie on the alluvial plain, on flat ground that rules out any gravity-fed solution. Surface water is unavailable or insufficient in the dry season (March to May) and traditional wells (7 to 15 m) dry up every year. Deep groundwater is therefore the only reliable and durable option, as evidenced by numerous field observations (numerous individual wells at a depth of about 50 m in the basin, with constant flow rates).

The technical model adopted for each village is: a safe community borehole; a submersible pump powered by solar energy, where appropriate in hybrid configuration with the EDL grid; a ground-level reservoir with a settling-filtration compartment and a storage compartment; and a pressurized distribution network fed by booster pumps and fitted with household meters.

The Client holds no subsurface data of its own for the proposed sites. Borehole sitting cannot therefore rest on surface criteria alone. This contract accordingly begins with a study and geophysical investigation stage intended to locate the deep aquifer and to position each borehole on an evidence-based target and ideally on public land.

## 1.2 Two-stage structure and decision gate

The contract is awarded to a single Contractor and executed in two stages separated by a decision gate. Stage 2 is not committed at the time of award.

| Stage | Status at award | Content |
| --- | --- | --- |
| Stage 1 — Geophysical investigation and siting | Firm | Desk review of the data supplied by the Client, electrical resistivity survey in the three villages, targeting report, joint site confirmation and siting minutes |
| Decision gate | — | The Client reviews the targeting reports and decides, village by village, whether to proceed to Stage 2 |
| Stage 2 — Primary boreholes | Conditional tranche | One primary borehole per village, drilled, completed, developed, tested and documented — three boreholes |
| Stage 2 — Standby boreholes | Option | One standby borehole per village, ordered separately by the Client — three boreholes |

The primary purpose of the first stage is to establish whether a productive deep aquifer can be reached at each of the three villages. Should the geophysical results be unfavourable in a given village, the Client may drop that village from Stage 2, or drop Stage 2 altogether, without any compensation being due beyond payment for Stage 1 as executed. The Contractor shall not claim any indemnity in respect of conditional tranches or options that are not ordered.

A maximum of six boreholes is to be priced (three primary, three standby). The Client gives no undertaking as to the number that will actually be ordered.

## 1.3 Scope of services

Stage 1 — Geophysical investigation and siting

- desk review of the documentation supplied by the Client and preparation of a hydrogeological orientation note for each village, with no site visit at this stage;

- electrical resistivity survey in each village, with the acquisition, processing, inversion and interpretation of the data;

- a targeting report proposing, for each village, at least two ranked drilling targets with recommended total depth and screen setting;

- joint site confirmation with the project team and the village committee, and signature of the siting minutes, carried out during the same mobilization as the geophysical survey.

Stage 2 — Drilling works

- drilling, casing, well completion and sanitary grouting of each borehole;

- development of the borehole until clear, sand-free water is obtained;

- pumping tests (step-drawdown test, constant-rate test and recovery monitoring) and their hydrodynamic interpretation;

- collection of a water sample and its conditioned handover to the Client; laboratory analysis is an optional item;

- securing of the wellhead (casing stick-up, lockable cap, vent) pending permanent equipment;

- full reinstatement of the site and disposal of drilling sludge and cuttings;

- preparation of the borehole completion report (geological and technical logs, test records, hydrodynamic interpretation, summary sheet).

## 1.4 Exclusions

The following are expressly excluded from this contract and are carried out by the Client or under separate contracts:

- supply and installation of the permanent submersible pump, its cable, level probe, rising main and control panel;

- supply and installation of solar equipment, booster pumps and any permanent electrical installation;

- construction of the reservoir and treatment train, and laying of the distribution network;

- permanent wellhead equipment (flange, sanitary seal, permanent cable entries), which the Client will fit when the pumping equipment is installed;

- water demand assessment and system sizing, which are the subject of a detailed hydraulic study prepared by the Client and issued to the Contractor (article 3.1).

The Contractor shall nonetheless guarantee that its borehole is compatible with this future equipment: inside diameter of the casing, height and geometry of the casing stick-up, clearance around the wellhead, and the design data set out in the completion report (operating yield, dynamic water level, recommended pump setting depth).

## 1.5 Contract structure and cost control

The contract is structured so as to confine expenditure to what is strictly necessary and to allow the Client to make choices during execution. The following principles are contractual and are reflected in the bill of quantities (Annex A):

- Single mobilization. All three villages lie in Paksan district. Mobilization and demobilization of the geophysical crew, and of the drilling rig, are each paid as a single lump sum for the whole campaign (same field mission).

- No separate mobilization for site confirmation. The joint site visit and the signature of the siting minutes are carried out during the geophysical campaign.

- Capped paid depth. The maximum paid depth is 80 m per borehole (article 5.2); beyond that, prior written agreement is required.

- Options priced but not committed. Items marked OPTION in the bill of quantities must be priced but are ordered only on written instruction; they are excluded from the comparison of offers. The Client may carry them out through village labour or by its own means.

- Water analysis. The Client operates its own water quality monitoring arrangement. Sampling and conditioning are the Contractor's responsibility; laboratory analysis is optional (article 7).

## 1.6 Contract documents

The contract is governed, in decreasing order of precedence, by: (i) the signed contract agreement; (ii) these technical specifications and their annexes; (iii) the bill of quantities completed by the Contractor; (iv) the Contractor's technical offer; (v) the legislation in force in Lao PDR relating to groundwater abstraction and construction.

These specifications is issue in English to ensure the clarity of technical information.

# 2. Target villages and design duty

## 2.1 Villages, population and location

All three villages are in Paksan district, Bolikhamxay Province. The coordinates below identify the village centre and define the area within which the geophysical survey is to be carried out; they are not drilling locations. The drilling location is determined by the survey (articles 3.2 to 3.5).

| Village | Population | Coordinates (WGS 84) | Boreholes to be priced |
| --- | --- | --- | --- |
| Khamphai | 632 inhabitants, 129 households | 18°29'57.3"N 103°48'35.0"E | 1 primary (conditional) + 1 standby (option) |
| Thongwarn | 489 inhabitants, 111 households | 18°23'54.0"N 103°50'46.5"E | 1 primary (conditional) + 1 standby (option) |
| Nongsaman | 514 inhabitants, 96 households | 18°22'32.7"N 103°50'35.8"E | 1 primary (conditional) + 1 standby (option) |

## 2.2 Purpose of the standby borehole

The standby borehole is a second, independent water point intended to secure the supply of the village: it provides redundancy in the event of failure, maintenance or clogging of the primary borehole, and allows the two boreholes to be operated alternately. It is ordered by the Client on written instruction and priced at the same unit rates.

The standby borehole is not a remedy for an unproductive primary borehole. Where a primary borehole fails to meet the acceptance criteria of article 6.5, the Contractor shall drill a replacement at its own cost under article 6.6. The two arrangements are distinct and must not be confused in the offer.

Where a standby borehole is ordered, it shall be located ideally close from the primary borehole (not more than 50 meters away) and shall be drilled on the second target identified in the targeting report.

## 2.3 Design duty of the boreholes

Each borehole shall be designed and constructed to accept and to sustain the following duty, which corresponds to the pumping equipment the Client will procure:

| Parameter | Design value |
| --- | --- |
| Pump type | 4" submersible pump, procured and installed by the Client (not in this contract) |
| Nominal flow | 8 m³/h |
| Total dynamic head | approx. 60 m (6 bar) – depending on drilling conditions |
| Required inside diameter of casing | 6” diameter, to accept a 4" pump (≈ 100 mm), its cable and its level probe |
| Required sustainable yield | Measured operating yield of at least 10 m³/h during the constant-rate test in November. After the seasonal correction of article 6.5 this gives a usable dry-season yield of approximately 7.5 - 8 m³/h, which is the value adopted for design |
| Storage and filling regime | Each village will be equipped with ground storage of approximately 40 - 50 m³ (depending on village size). The borehole is not required to sustain 10 m³/h continuously: it must be able to fill the reservoir with a single pump within about 4 to 6 hours of operation (operational goal) |
| Dynamic water level at design duty | Not deeper than 31 m below ground level, and remaining at least 6 m above the top of the screen |
| Pump setting depth | At least 8 m below the corrected dynamic level and at least 6 m above the top of the screen — approximately 39 m for a borehole of the nominal design |

The Contractor shall confirm in its technical offer that the proposed well design accepts a 4" pump of this duty over the full cased length and shall state the real inside diameter of the casing it intends to supply.

# 3. Stage 1 — Geophysical investigation and siting

## 3.1 Desk review — no site visit

No site visit is required at this stage. Within five days of notification the Client shall issue to the Contractor a complete documentation package for each village, comprising:

- a detailed hydraulic study prepared by the Client: population served, daily demand, design flow, demand profile, schematic of the proposed system and sizing constraints;

- the water access assessment report (activity 1.1.1) and the results of the water quality monitoring campaigns carried out since 2026;

- an inventory of existing water points: traditional wells and known private boreholes, with depth and static water level where available;

- a village location plan, the land available, and the position of the EDL low-voltage network.

On this basis the Contractor shall prepare, for each village, a short hydrogeological orientation note covering:

- the regional geological and hydrogeological setting and the expected lithological sequence, drawing on publicly available data and on the Contractor's experience in comparable settings;

- the expected depth of the top and base of the deep aquifer, and the expected thickness of the low-permeability transition horizon;

- the drilling method envisaged and the technical risks anticipated (unstable alluvium, loss of circulation, karst, mineralised horizon);

- the proposed layout of the geophysical lines, plotted on the village plan, with justification of the orientation and length adopted;

- where applicable, a list of any further data considered necessary.

The orientation note is due no later than ten (10) calendar days after notification of the contract and is a precondition to mobilization of the geophysical crew.

## 3.2 Geophysical survey

The purpose of the survey is to locate the most favorable drilling positions within the available land, to establish in advance the depth of the top and base of the deep aquifer, and to rule out clay-dominated zones, barren pinch-outs and excessively mineralized horizons.

Two independent targets are required in each village, one for the primary borehole and one for the standby borehole. The survey layout shall be designed accordingly.

| Parameter | Minimum requirement |
| --- | --- |
| Method | 2D electrical resistivity tomography (ERT). Wenner–Schlumberger array is required for depth determination; dipole-dipole may be added at the Contractor's initiative for lateral resolution |
| Vertical electrical soundings | Schlumberger soundings with AB/2 ≥ 250 m may be used to complement the 2D lines and to confirm the base of the aquifer. At least one sounding shall be carried out at each retained target |
| Number of lines | At least two ERT lines per village, laid out so as to cover both candidate targets. A third line may be ordered on written instruction where the interpretation remains ambiguous |
| Electrode spacing | 5 to 10 m, selected and justified by the Contractor with regard to the target depth; the spacing adopted shall be stated in the orientation note |
| Depth of investigation | Effective depth of investigation of at least 80 m, with sufficient sensitivity at 65 m to resolve the top of the target aquifer |
| Data quality control | Stacking with a standard deviation of 3 % or less; repetition of doubtful sequences; documented removal of outliers |
| Positioning | GPS survey (WGS 84) of both ends and the mid-point of each line, accuracy ≤ 3 m; relative levelling along the line to allow topographic correction. Surveying work (topography) can be carried out by the CCL and material can be provided. |

A geophysicist or hydrogeologist with demonstrated experience of resistivity methods applied to groundwater exploration shall lead this stage; the curriculum vitae shall be attached to the offer, and this person shall sign the targeting report.

## 3.3 Targeting report

On completion of the survey the Contractor shall submit a targeting report for each village (1 report for the three villages is fine), containing:

- a reminder of the orientation note and a location map of the lines actually run, plotted on the village plan;

- the inverted resistivity sections, presented both raw and interpreted, under both inversion norms, together with the acquisition and inversion parameters;

- correlation with the existing water points supplied by the Client, and any departure between the expected and the observed model;

- an interpretative geological model giving the top and base of the horizons identified, the thickness of the low-permeability horizon and the depth to the top of the target aquifer;

- at least two ranked targets, each with GPS coordinates, recommended total depth, recommended screen setting, expected order of magnitude of yield and the confidence attached to it;

- the risks identified at each target (clay pinch-out, karst, limited saturated thickness, indication of mineralised water) and the corresponding drilling precautions;

- an explicit and reasoned opinion on feasibility, and in particular on a measured yield of 10 m³/h, as set out in article 2.3, appears achievable at each target. Where no favorable target can be identified within the available land, the Contractor shall say so plainly and may propose an extension of the survey area; the Client will then decide how to proceed.

## 3.4 Siting criteria

In addition to the outcome of the geophysical survey, the location adopted shall satisfy all of the criteria below, in the order of priority given. Where a geophysically favorable target fails one of these criteria, the next target is examined with the project staff.

| Priority | Criterion | Requirement |
| --- | --- | --- |
| 1 | Sanitary protection | At least 30 m from any latrine, septic tank, soakaway or burial ground; 50 m from any livestock pen, waste dump or store of agricultural chemicals; outside the run-off catchment of any piggery or slaughterhouse |
| 2 | Flood-free ground | Natural ground above the highest known flood level plus 0.50 m; failing that, raising of the platform at the cost of the contract |
| 3 | Land tenure | Communal land (preferred), or private land subject to a written, voluntary and documented transfer to the village, countersigned by the village head and the district (see article 4.3) |
| 4 | Electricity connection | Less than 100 m from the EDL low-voltage network; beyond that distance the cost of extension is subject to the Client's approval |
| 5 | Access | Trafficable access for a truck-mounted drilling rig |
| 6 | Interference | 20m from any existing private borehole, unless justified on hydrogeological grounds |

## 3.5 Joint site confirmation

The joint site visit is carried out during the geophysical campaign, in the presence of the Client's representative, the village head or the village head's representative, and representatives of the Provincial health office, the district Nam Saat and the district of Agriculture and Environment.

Siting minutes are drawn up and signed by all parties, recording:

- the GPS coordinates of the drilling location (WGS 84) and the approximate elevation on ground;

- the location plotted on the corresponding resistivity section, and the reference of the geophysical line from which it is derived;

- the distances to dwellings, latrines, existing water points, the nearest EDL line;

- a dated photographic record;

- express confirmation that the village committee has approved the location (CCL part with GoL partners);

- a record of access constraints and any particular difficulties.

No drilling may start before these minutes are signed and the targeting report approved. Moving the drilling location by up to 100 m from the approved geophysical target, to accommodate a land or access constraint, gives rise to no additional payment; beyond that distance a partial re-survey may be instructed at the unit rates of the bill of quantities.

## 3.6 Decision gate

The Client has ten (10) working days from receipt of the last targeting report to notify its decision. That decision may be:

- to proceed to Stage 2 in all three villages;

- to proceed to Stage 2 in one or two villages only;

- not to proceed to Stage 2, where the geophysical results do not establish a reasonable prospect of reaching the design duty.

Mobilization of the drilling rig may not take place before this written decision is issued. Stage 1 is paid in full whatever the decision.

Responsibility. The targets are proposed by the Contractor on its own technical responsibility. The Client's approval addresses the coherence of the reasoning, compliance with the criteria of article 3.4 and the acceptability of the location to the village; it transfers none of the technical risk. This provision is the basis for the Contractor's replacement obligation at article 6.6, and the Contractor shall take it into account when pricing Stage 2.

# 4. Obligations prior to commencement

## 4.1 Unexploded ordnance — chance find procedure

The sites are within village boundaries, on land long built on, cultivated or otherwise developed. The Client has accordingly assessed the residual unexploded ordnance risk as low and does not require prior clearance. This assessment is recorded in a risk note annexed to the siting minutes for each site.

The Contractor remains bound to apply the following procedure on the chance find of any ordnance or suspect object, whether at the surface, in the cuttings, during the placing of electrodes or during drilling:

- immediate stoppage of all mechanical operations and shutdown of equipment;

- absolute prohibition on handling, moving, uncovering or covering the object;

- evacuation of personnel and of any other person present, and marking out of a safety perimeter;

- immediate notification of the Client, the village head and the district authorities, who will refer the matter to the accredited operator;

- resumption of work only on the Client's written authorization.

This procedure shall be reproduced in the Contractor's HSE plan (article 9.1) and brought to the attention of all site personnel, including locally recruited labor, before commencement. Any resulting stoppage entitles the Contractor to an extension of the contract period, without indemnity.

## 4.2 Permits and authorizations

The Contractor shall be duly registered in Lao PDR and hold the authorizations required to carry out water well drilling. It shall provide with its offer the operating licence issued or its provincial authority, together with its tax compliance certificate.

The Contractor shall assist the Client in preparing the groundwater abstraction declarations or permits required by PAE and PHO and shall submit, within the statutory time limits, the data required (coordinates, depth, log, yield) for registration of the boreholes in the provincial water point register.

## 4.3 Land access and community information

Making the land available is the responsibility of the Client and the village. It is formalized by a written agreement signed by the owner where applicable, the village head and the district authority, confirming that no involuntary physical or economic displacement occurs and that the community has permanent access to the borehole.

The Contractor shall inform the village committee at least 72 hours before arriving, for the geophysical campaign as well as for drilling, and shall observe the agreed working hours. Geophysical lines crossing cultivated plots require the prior agreement of the farmers concerned. Any damage to crops, fences or property on the site or on the access route shall be the subject of a prior joint record and shall be settled amicably.

# 5. Technical specifications for the boreholes

## 5.1 Drilling method and equipment

The construction program for each borehole follows from the approved targeting report (article 3.3): recommended total depth, recommended screen setting, and the precautions attached to the risks identified. The regional expectation remains alluvium and weathered material in the upper part, resting on a sandstone or carbonate bedrock.

The drilling method is left to the Contractor, provided it is suited to the formations encountered and secures both hole stability and sample quality: down-the-hole hammer with compressed air in consolidated formations; direct-circulation rotary with drilling fluid in unconsolidated formations; temporary or permanent surface casing through unstable alluvium.

The rig provided shall be capable of reaching 90 m in all formations. The following minimum characteristics are required and will be verified at the opening of offers against supporting documents (technical sheets, dated photographs, serial numbers). Equipment of equivalent or better characteristics is acceptable where equivalence is demonstrated.

| Equipment | Minimum characteristic |
| --- | --- |
| Drilling rig | Pull-up capacity ≥ 1,500 kg; rotation torque ≥ 1,300 N·m; hydraulic power unit ≥ 13 hp |
| Drilling compressor (DTH) | Pressure ≥ 10 bar; delivery ≥ 7 m³/min (≈ 120 L/s). 12 bar is preferable for air-lift development at 65 m |
| Development compressor | Pressure ≥ 10 bar; delivery ≥ 5 L/s, independent of the drilling compressor |
| Mud pump | Pressure ≥ 10 bar; delivery ≥ 18 L/s |
| Drill string | At least 90 m available |
| Test pumping equipment | Variable-rate submersible test pump capable of at least 12 m³/h at 40 m, with generator, volumetric flow meter, and dip meter graduated to the centimeter |
| Geophysical acquisition system | Automatic multi-electrode resistivity meter |

NB: The Contractor is free to offer better equipment, or any equipment that he judged more adapted provided he informs the project advisor.

## 5.2 Depths and diameters

| Parameter | Minimum requirement |
| --- | --- |
| Design depth | Fixed borehole by borehole by the approved targeting report; expected order of magnitude 65 m. Minimum accepted depth 60 m; maximum paid depth 80 m (beyond that, prior written agreement of the Client) |
| Drilled diameter — cased section | ≥ 165 mm (6½"), giving an annular space of at least 40 mm around the casing |
| Drilled diameter — surface hole | ≥ 220 mm (8½") through the unconsolidated surface formations |
| Inside diameter of casing | ≥ 110 mm, measured as the real inside diameter and not the nominal diameter. This value is binding: it governs the passage of the 4" submersible pump (≈ 100 mm), its cable and its level probe. Given the wall thicknesses of the Thai standard commonly available, it requires casing of DN 125 mm as a minimum |
| Top of screen | Binding: no screen above 45 m depth, whatever water strikes are encountered above that level |
| Verticality / deviation | Deviation less than 1° per 30 m; verified by the free passage, over the whole cased length, of a rigid dummy 6 m long and of a diameter equal to the inside diameter of the casing less 10 mm |

Nomenclature. The boreholes are nominal 6-inch boreholes: a drilled diameter of at least 165 mm (6½") in the cased section, completed with DN 125 mm PVC casing. This combination leaves a radial annular space of about 20 mm, which is the accepted practice in Lao PDR for a community borehole of this size and which the Client has adopted deliberately in order to contain cost.

The Contractor shall satisfy itself that it can place the gravel pack and the annular grout correctly within that annulus. Where it considers a larger diameter necessary in the formations expected, it may offer that as a priced variant, clearly identified as such; the variant will not be used in the comparison of offers.

The final depth of each borehole is fixed by the Client on the Contractor's proposal, in the light of the water strikes observed, the lithological log recorded during drilling and any departure from the geophysical model. The Contractor shall immediately inform the Client of any significant water strike, any total loss of circulation, any marked change of formation, and any marked departure between the observed lithology and the model set out in the targeting report.

## 5.3 Target aquifer and isolation of the shallow aquifer

The purpose of the borehole is to capture the free-standing (unconfined) aquifer identified by the geophysical survey — on available data between 48 and 65 m depth — and not the shallow aquifer exploited by village wells (7 to 15 m) and private boreholes (25 to 40 m).

This requirement is fundamental. Existing private boreholes abstract small volumes, of the order of 0.5 to 1 m³ per day per household, but there are many boreholes in this area. The community borehole will abstract up to 10 m³/h, and daily production is expected to be around 30 to 50 m³. The sustained drawdown that results is liable to induce downward leakage from the shallow horizons, which are vulnerable to domestic pollution (latrine pits) and agricultural pollution (fertilizer and pesticides). Good water quality observed at low abstraction is therefore no guide to quality under community abstraction.

Protection of the borehole accordingly rests less on its total depth than on the tightness of its annulus. The Contractor shall:

- penetrate the shallow aquifer without screening it, whatever water strikes are encountered; no screen may be set above 45 m depth;

- grout the annulus continuously from the top of the bentonite seal to ground level, that is over some 43 m, in accordance with article 5.6;

- report immediately to the Client any significant water strike above 45 m: it may on no account justify stopping drilling early or raising the screen;

- continue drilling until a productive horizon is identified below the low-permeability transition, within the maximum paid depth.

Monitoring of mineralization during drilling. So that any excessively mineralized deep horizon is detected before the borehole is completed, the Contractor shall measure the electrical conductivity and the temperature of the water discharged by air-lift every 5 m from 40 m depth, and at every water strike. The values shall be entered on the daily drilling record. Any value above 1,200 µS/cm, the Lao national drinking water threshold, shall be reported to the Client without delay. Above 1,400 µS/cm, the WHO guideline value, the Client will decide whether to continue, to stop or to abandon the borehole.

First borehole of the campaign. The first borehole shall be executed with particular care in sampling and lithological description. Its geological log, water strikes and test results serve as a reference to calibrate the geophysical model and to fix the final depth, screen setting and grouting program for the following boreholes. The Contractor shall transmit the provisional log of that borehole, together with a one-page note comparing the observed lithology with the resistivity model, within 5 days of its completion.

## 5.4 Sampling and drilling records

- Collection of a representative cuttings sample every meter and at every change of formation, bagged, numbered and labelled (site, depth, date).

- Storage of the samples in a compartmented cuttings box, handed over to the Client at provisional acceptance.

- Maintenance of a daily drilling record showing: depth reached, rate of penetration, tool used, formations encountered, water strikes (depth and air-lift estimated yield), fluid losses, conductivity readings and incidents.

- Measurement of the static water level after stabilization, before and after completion.

## 5.5 Casing, screens and gravel pack

| Item | Specification |
| --- | --- |
| Plain and screened casing | Food-grade, non-toxic PVC-U to the Thai standard commonly used in Lao PDR, wall thickness 8.5 or 13.5 mm, male-female threaded joints (solvent welding is prohibited). Manufacturer's marking visible on the pipes. The nominal diameter follows from the inside diameter requirement is DN 125 mm as a minimum (article 5.2) |
| Screen | Factory machine-slotted (site sawing is prohibited), aperture 1.0 mm, open area ≥ 6 % (8 % preferred). Screen length matched to the water strikes and to the interval recommended in the targeting report, with a minimum of 12 m; 18 m or more is preferred where the aquifer allows, given the design duty of 10 m³/h |
| Sump | Plain pipe of at least 3 m at the base of the borehole, closed by a threaded watertight bottom plug |
| Centralisers | PVC centralizers every 6 m on the completed string, and systematically at the top and bottom of the screen |
| Gravel pack | Washed, rounded, graded siliceous gravel 2–3 mm, consistent with a 1.0 mm screen aperture (to be adjusted to the grain size of the aquifer formations). Placed by controlled gravity from 2 m below the bottom screen to 3 m above the top screen, and topped up after development. The gravel shall be disinfected before placing by watering with a 50 mg/L chlorine solution |
| Bentonite seal | Bentonite (pellets or compacted granules) of at least 2 m thickness above the gravel pack, hydrated before grouting |

## 5.6 Sanitary annular grouting

The annulus shall be grouted in full from the top of the bentonite seal to ground level, that is over some 43 m. This grouting is the principal protection of the borehole: it prevents vertical circulation between the shallow aquifer and the horizon captured, including under the drawdown induced by community abstraction. It shall be placed by tremie pipe lowered to the base of the zone to be grouted, from the bottom upwards, so as to avoid bridging.

- Portland cement grout CEM I or CEM II, water/cement ratio between 0.45 and 0.50, with 3 to 5 % bentonite where appropriate.

- Measurement of the volume of grout placed against the theoretical annular volume; immediate topping up in the event of shrinkage after setting. A difference of more than 20 % between placed and theoretical volume shall be reported and investigated before work continues.

- Minimum setting time of 24 hours before development operations resume.

- Grouting is a hold point: it shall be witnessed by the Client's representative, who verifies the volume of grout placed against the theoretical volume and the return of grout to the surface.

## 5.7 Development

Development shall be carried out after the grout has fully set, by air-lift and alternate surging, supplemented where necessary by alternate pumping or by brushing the screened string. The use of chemical dispersants requires the CCL project advisor’s prior written agreement.

- Minimum development time: 6 effective hours per borehole, continued as long as necessary until the criteria below are met.

- Control of the development rate: the abstraction rate shall not exceed the expected operating yield by more than 50 %. Development at an excessive rate causes abrupt breakdown of the filter, draws fine particles from the formation and leaves the borehole persistently turbid. Development shall be progressive, with the rate increased in steps starting from one quarter of the target rate.

- Completion criteria: clear and stable water, turbidity below 5 NTU, sand content below 5 g/m³ (measured with an Imhoff cone or sand tester), and a stabilized specific capacity.

- Development shall be carried out over the full screened length, in successive sections, and not solely at the base of the borehole.

- Development water shall be directed to the mud pit and shall on no account be discharged into a ditch, a paddy field or a watercourse.

## 5.8 Disinfection

After development and before the pumping tests, the borehole shall be disinfected by introducing a chlorine solution of 50 mg/L available chlorine into the water column, held in contact for at least 12 hours, then purged by pumping until residual chlorine has disappeared. The operation shall be repeated after any subsequent intervention in the borehole.

# 6. Pumping tests and acceptance

## 6.1 General

The pumping tests are the basis on which the Client will size and procure the permanent pumping equipment, and they govern acceptance of the borehole. They shall be carried out in the presence of the CCL project team (advisor & technician at least) and GoL counterparts (PHO, DHO, DAE) representative, who countersigns the measurement records.

The Contractor shall provide: a variable-rate submersible test pump of sufficient capacity to reach at least 12 m³/h at 40 m, so that the design yield can actually be tested and exceeded; an accurate flow measuring device (totalising volumetric meter, calibrated tank or V-notch weir — visual estimation is prohibited); an automatic recording piezometer; a stopwatch; a multi-parameter field measuring device (temperature, pH, conductivity, turbidity); and the discharge pipe required to convey the pumped water, hydraulically downstream, without causing erosion or recirculation back into the aquifer under test.

## 6.2 Step-drawdown test

A step-drawdown test shall be carried out to determine head losses and the critical yield of the borehole:

- four steps of one hour each, at increasing rates, run continuously (or separated by full recovery, according to the method adopted and justified);

- indicative rates: 25 %, 50 %, 75 % and 100 % of the maximum rate estimated during development;

- dynamic water level readings at 0.5 — 1 — 2 — 3 — 4 — 5 — 7 — 10 — 15 — 20 — 30 — 40 — 50 — 60 minutes in each step;

- recovery monitoring for at least 60 minutes after the last step;

- measurement of the rate at each reading, held constant within ± 5 %;

- the drawdown reached in the last step shall not exceed 60 % of the available water column above the top of the screen.

## 6.3 Constant-rate test

Once the water level has recovered to within 10 % of the maximum drawdown reached, a constant-rate test shall be carried out for at least 12 consecutive hours (one working day), at a rate of approximately 75 % of the critical yield determined by the step test, and in any event at a rate sufficient to establish whether a yield of 10 m³/h can be sustained over the test.

- Dynamic water level readings at 1 — 2 — 3 — 5 — 7 — 10 — 15 — 20 — 30 — 40 — 50 — 60 minutes, then every 30 minutes to the end of the test.

- Checking and recording of the rate every 30 minutes; the rate shall be held constant within ± 5 %.

- Field measurements at the start, mid-point and end of the test (if possible): temperature, pH, electrical conductivity, turbidity.

- Recovery monitoring for at least 3 hours, or until 90 % of the drawdown has recovered, at the same time intervals as during drawdown.

- Where two boreholes are drilled in the same village, the second borehole shall serve as an observation well: its water level shall be monitored during the constant-rate test in order to quantify interference. This measurement is required before the two boreholes may be operated simultaneously.

Optional extension. Where the dynamic water level has not stabilized at the end of the 12 hours, or where the interpretation suggests a boundary effect, the Client may instruct extension of the test to 24 hours. This extension is priced separately in the bill of quantities and is payable only on written instructions.

## 6.4 Interpretation

The Contractor shall produce a hydrodynamic interpretation signed by a hydrogeologist or qualified engineer; estimation of transmissivity; calculation of specific capacity; determination of the critical yield and of the recommended operating yield in continuous 12-hour operation; the seasonally corrected value; and the recommended setting depth for the permanent pump. That depth shall be at least 8 m below the corrected dynamic level and 6 m above the top of the screen.

The interpretation shall state expressly whether the borehole sustains a measured yield of 10 m³/h at a dynamic level compatible with a 4" pump set as above, and what corrected yield this gives for design, and shall include a short comparison with the geophysical model: agreement or departure between the depth and thickness of the productive horizon predicted in the targeting report and those actually encountered, and the lessons for the following boreholes.

## 6.5 Acceptance criteria

The measured operating yield (Qm) is the yield that can be sustained over 12 hours of continuous pumping with a stabilized dynamic level remaining at least 3 m above the top of the upper screen.

Seasonal correction. The tests are carried out in November, immediately after the rainy season, so the levels measured correspond to the annual piezometric maximum and the yield obtained is a high value. Low water occurs between March and May. The yield adopted for sizing is accordingly 0.75 × the measured yield. The thresholds below apply to the yield measured in November, before correction; the Contractor shall state both values in its interpretation note.

| Yield measured in November | Corrected yield (× 0.75) | Classification and consequence |
| --- | --- | --- |
| Qm ≥ 10 m³/h | ≥ 7.5 m³/h | Compliant. Borehole accepted and paid in full. The Client may order the standby borehole for redundancy |
| 6 ≤ Qm < 10 m³/h | 4.5 to 7.5 m³/h | Acceptable. Borehole accepted and paid in full. The Client may order the standby borehole so that the pair together meets the design yield, or may accept a longer daily filling time for the reservoir |
| 4 ≤ Qm < 6 m³/h | 3 to 4.5 m³/h | Marginal. Decision of the Client: retention of the borehole as a supplementary water point, at a payment agreed between the parties, or abandonment. Where retained, article 6.6 does not apply |
| Qm < 4 m³/h | < 3 m³/h | Unproductive. Borehole plugged in accordance with article 6.7. Not paid. The Contractor shall drill a replacement at its own cost in accordance with article 6.6 |

## 6.6 Unproductive boreholes — the Contractor's replacement obligation

Each borehole is located on a target selected by the Contractor on the basis of its own geophysical survey and its own targeting report. The risk of an unproductive borehole therefore lies with the Contractor.

Where a borehole is classified unproductive under article 6.5, the Contractor shall, at its own cost and within the contract period:

- plug and abandon the borehole in accordance with article 6.7;

- carry out any complementary geophysical investigation needed to identify a new target, including additional lines or soundings;

- submit a revised targeting report to the Client for approval;

- drill, complete, develop and test a replacement borehole at the new target.

Financial compensation may be paid by the project, subject to prior written agreement between the parties.

Limit of the obligation. This obligation is limited to one replacement borehole per village. Where the replacement borehole is itself unproductive, the parties shall meet to decide whether to continue, on terms to be agreed, or to terminate the works in that village by mutual agreement, without indemnity on either side.

Exceptions. The obligation does not apply where the Client instructed a location against the written and reasoned technical advice of the Contractor, or where the Contractor stated in its targeting report that no favourable target existed within the available land and the Client nonetheless instructed drilling. In both cases the borehole is paid at the unit rates of the bill of quantities.

## 6.7 Plugging and abandonment

Any abandoned or unproductive borehole shall be plugged in full, from the base to the surface, with cement grout placed by tremie pipe, so as to prevent contamination of the aquifer and any risk of a fall. Plugging shall be recorded in joint minutes.

# 7. Water quality

A sample shall be taken during the last hour of the constant-rate test, after sufficient purging, in sterile bottles kept in a cool box at 4 °C. Sampling, conditioning, labelling are an obligation falling within the remit of the project owner, the CCL, and the provincial authorities (PHO)

The Client, which operates its own water quality monitoring arrangement in the project villages, reserves the right to have the analyses carried out by its own means and will collect himself samples to conduct full water quality analysis in close collaboration with the Nam Saat.

The following parameters will be determined as a minimum, by reference to the Lao national drinking water standards and, failing that, to the WHO guideline values:

| Group | Parameters |
| --- | --- |
| Field measurements (mandatory, Contractor's obligation) | Temperature, pH, electrical conductivity, turbidity, at the start, mid-point and end of the constant-rate test |
| Organoleptic and physical | Turbidity, colour, odour, total dissolved solids |
| Major ions | Total hardness, chloride, sulphate, nitrate, nitrite, ammonium, fluoride |
| Metals and trace elements | Total iron, manganese, arsenic |
| Bacteriological | Total coliforms, Escherichia coli (or thermotolerant coliforms) |

Iron and manganese warrant particular attention: the assessment found groundwater frequently laden with sediment and yellowish in colour in the villages concerned. The results govern the sizing of the settling and filtration compartment of the reservoir. Where a parameter that the planned treatment train cannot address exceeds the standard — arsenic in particular — the Client reserves the right to abandon the borehole; the Contractor is then paid for the borehole as constructed and article 6.6 does not apply. At present, based on the analysis of all the boreholes (8 boreholes in the area), no arsenic contamination or high concentrations of iron and manganese have been reported.

# 8. Securing the wellhead

The boreholes will be drilled several months before the Client installs the permanent pumps, so their immediate protection is a major contractual requirement. A borehole left open or inadequately protected is at once a public health risk (direct contamination of the aquifer), an accident risk for children and livestock, and a risk of irreversible damage to the borehole (falling objects, silting).

Permanent wellhead equipment — flange, sanitary seal, cable and probe entries — will be fitted by the Client when the pumping equipment is installed and is not part of this contract. The Contractor is responsible only for the temporary securing described below, the cost of which should remain modest.

## 8.1 Wellhead — mandatory

- The casing shall stand at least 0.50 m and at most 0.80 m above finished ground level, and shall be cut cleanly and square to its axis so that a sanitary seal can be fitted later.

- The borehole shall be closed by a galvanized steel or cast-iron cap of at least 3 mm thickness, fitting over or clamped around the casing, and secured with a padlock. Two sets of keys shall be handed over, one to the village water management committee and one to the Client.

- flange or adaptor is required; the arrangement shall be removable without cutting or damaging the casing, in order to properly install the pumping system.

- Where no apron is ordered (article 8.2), the Contractor shall place a compacted temporary backfill around the borehole, graded to shed run-off away from the casing.

No borehole may be left without the casing cut square and the cap fitted and locked. Annular grouting to ground level (article 5.6) may likewise not be deferred.

## 8.2 Concrete apron / slab — optional

The concrete apron is an optional item. It is priced separately in the bill of quantities and is ordered only on the Client's written instruction. Failing such an order it will be built by village labour under the technical supervision of the project team, in accordance with the division of tasks set out in the financing agreement, without the Contractor being entitled to any indemnity. In either case the specifications below apply, and they are also the technical reference for the village-built works.

- Reinforced concrete slab at 350 kg/m³, minimum dimensions 2.00 m × 2.00 m and 0.15 m thick, reinforced with welded mesh.

- Slab integral with the casing and fully watertight at the contact, cast after the annular grouting and on a compacted base.

- Fall of at least 2 % from the wellhead outwards, with a perimeter kerb and a drainage channel taking water to a soakaway or drainage area at least 5 m from the borehole.

- Concrete made with washed 3–25 mm aggregate and 0–2.5 mm sand, free of organic matter.

- Wet curing by daily watering for 7 days before any traffic or loading.

- The borehole number, date of construction, total depth and project name to be inscribed in the fresh concrete.

## 8.3 Securing the site pending equipment

- Temporary fencing of the immediate perimeter (optional item, or built by village labour): wire or timber fence at least 1.20 m high over 4 m × 4 m, with a closing gate. It may be omitted where the site is already enclosed; the locked wellhead protection remains mandatory in all cases.

- Bilingual Lao-English information board giving the borehole identity, the project and the contact for the village manager (optional item).

- Formal handover of the borehole to the village water management committee, with written instructions in Lao not to interfere with the borehole before the project team intervenes.

- Handover to the village committee of a copy of the borehole summary sheet (log, depth, yield, water levels), to be kept and produced on any later intervention by Nam Saat or by a maintenance contractor.

- A joint inspection visit shall be arranged one month after provisional acceptance to verify that the protection remains intact.

# 9. Health, safety, environment and social requirements

The project is co-financed by the French Development Agency, Fondation Groupe EDF, the City of Paris and the Rhin-Meuse Water Agency. The Contractor is accordingly bound by the environmental and social requirements applicable to those sources of finance, in addition to Lao legislation. These provisions apply to both stages of the contract, including the geophysical campaign. Failure to comply is a breach of contract that may lead to suspension of the works without indemnity.

## 9.1 Safety of personnel and third parties

- Preparation, before commencement, of a simplified health, safety and environment plan specific to the site, submitted to the Client for approval.

- Provision and mandatory wearing of personal protective equipment: helmet, safety boots, gloves, hearing protection near the compressor, eye protection, high-visibility vest.

- During the geophysical survey: marking of cables and electrodes, prior notice to the village, prohibition on approach during current injection, and supervision of any section of line near dwellings, schools or busy thoroughfares.

- Marking out and fencing of the working area; access prohibited to unauthorized persons, in particular children; permanent presence of a watchman whenever the rig is left on site.

- The borehole shall never be left open and unattended: temporary capping at the end of every shift.

- The mud pit shall be marked and signed at all times, and backfilled as soon as the works are complete.

- First aid kit on site, written medical evacuation procedure, contact details of the district health centre or hospital displayed.

- Notification of any accident or incident to the Client within 24 hours, including near misses.

- Third party liability insurance and workers' compensation cover for all personnel, evidenced before commencement.

## 9.2 Management of sludge, cuttings and drilling fluid

Management of drilling sludge is the principal environmental issue of the campaign. The contractor is required to set out its environmental safety plan with regard to sludge in detail (disposal, recovery, protection).

- Absolute prohibition on direct discharge of sludge, development water and test water into the paddy fields, ditches, ponds and watercourses of the Nam Sa basin.

- Exclusive use of drilling fluids made up of natural bentonite and food-grade biodegradable polymers; the use of diesel, waste oil and non-biodegradable foams is strictly prohibited.

- Settlement and drying of the sludge, removal of solid residues to an authorized site, and backfilling of the pit with the dried cuttings and the stripped topsoil, within 15 days of completion of the borehole.

- Grading and full reinstatement of the ground, the site being restored to its original or an improved condition, verified jointly with village authorities, GoL partners and CCL. Electrode holes from the geophysical campaign shall be backfilled and the plots crossed reinstated.

## 9.3 Hydrocarbons, waste and nuisance

- Storage of fuel and lubricants on an impermeable area with bunding of at least 110 % of the volume stored, at least 50 m from any water point.

- Collection and removal of all site waste, including PVC offcuts, packaging and domestic waste from personnel; burial and burning on site are prohibited.

- Limitation of noise: no drilling between 19:30 and 06:30 or on public holidays, save with the prior agreement of the village and the Client; damping of tracks where dust is raised near dwellings.

- Chance find procedure: where archaeological remains or burials are uncovered, work shall stop immediately, the area shall be protected and the authorities informed.

## 9.4 Social and integrity requirements

- Prohibition of child labour, in accordance with Lao legislation and the fundamental ILO conventions; no worker under 18 may be assigned to hazardous tasks.

- Prohibition of forced labour; written contract and pay at or above the legal minimum wage for all personnel, including locally recruited daily labour.

- Equal pay for women and men for equal work;

- Signature by all personnel of a code of conduct prohibiting sexual exploitation, abuse and harassment, and any form of violence or discrimination towards host communities.

- Prohibition of alcohol and drugs on site.

- Establishment, with the village committee, of a simple grievance mechanism: an identified contact point, a complaints register, resolution within 15 days and feedback to the complainant; the arrangement shall be made known to the village before commencement.

- Compliance with integrity rules: prohibition of any practice of corruption, fraud, collusion or facilitation payment; the Contractor shall not appear on the funding partners' debarment lists.

- Acceptance of the right of audit of the Client and the funding partners over the records relating to performance of the contract, which shall be kept for five years.

# 10. Deliverables

Deliverables are deliberately limited to essentials. They shall be submitted in English or Lao, in one paper copy and in electronic form (PDF, measurement data in a workable spreadsheet format, raw geophysical data and inversion files in their native format, photographs at full resolution). Template sheets are given in Annex B; the Contractor may use its own formats provided they carry all the headings requested.

| No. | Deliverable | Due | Expected content |
| --- | --- | --- | --- |
| D1 | Hydrogeological orientation note | Per village, 10 days after notification | Geological and hydrogeological setting, expected lithological sequence, expected depth of the aquifer, drilling method envisaged, proposed layout of the geophysical lines, risks anticipated |
| D2 | Targeting report | Per village, 10 days after the end of acquisition | interpretative geological model, at least two ranked targets with GPS coordinates, recommended depth and screen setting, expected yield and confidence, risks, and an opinion on the feasibility of the design duty. Raw data and inversion files attached |
| D3 | Siting minutes | Per site, before drilling starts | GPS coordinates, reference of the geophysical line, dimensioned sketch, photographs, UXO risk note, signatures of the parties. A one-page site organization and safety note is attached to the first set of minutes |
| D4 | Daily drilling record | Daily, countersigned on site | Progress, tool, formations encountered, water strikes and estimated yields, conductivity readings, fluid losses, incidents |
| D5 | Borehole completion report | Per borehole, within 15 days of completion | A single document comprising: metre-by-metre geological log; as-built technical log (diameters, casing, screen, gravel pack, bentonite, grouting, levels); development record; raw pumping test data tables; interpretation note signed by a hydrogeologist (critical yield, operating yield, corrected value, pump setting depth, comparison with the geophysical model, statement on the design duty); photographic record; A4 summary sheet (Annex B) |
| D6 | Acceptance minutes | Per site, at provisional acceptance | Record of the wellhead securing completed, of site and mud pit reinstatement, of the plugging of any abandoned borehole, and of the handover of the keys and the borehole summary sheet to the village committee |

A short campaign synthesis note shall accompany the last completion report: comparison of the boreholes, an overall comparison of the geophysical models with the lithologies encountered, conclusions on the hydrogeology of the area, operating and monitoring recommendations, and recommendations for extending the approach to the seven other villages of the project.

The completion report for the first borehole of the campaign (article 5.3) governs the launch of the following boreholes; its provisional log and the note comparing it with the resistivity model are due within 48 hours, without waiting for the full report.

# 11. Programme and site organisation

## 11.1 Indicative programme

| Phase | Period | Content |
| --- | --- | --- |
| Consultation and award | End September 2026 | Issue of the dossier, submission of offers by 18th September 2026, evaluation, notification, signature |
| Desk review (Stage 1) | Early October 2026 | Issue of the documentation package by the Client, hydrogeological orientation notes per village |
| Geophysical survey and siting (Stage 1) | Mid-October 2026 | Resistivity acquisition in the three villages in a single mobilization, joint site confirmation, siting minutes |
| Targeting reports and decision gate | Late October 2026 | Submission of the reports; the Client's written decision on Stage 2 within ten working days (hold point) |
| Drilling and testing (Stage 2) | November 2026 | Drilling, completion, development, pumping tests, wellhead securing |
| Reporting | Early December 2026 | Completion reports, interpretation, water analyses where applicable |
| Civil works (not in contract) | December 2026 – January 2027 | Construction of reservoirs and support structures |
| Pumping equipment (not in contract) | [January – February 2027] | Solar/hybrid submersible pumps, booster pumps on the EDL network, chlorination, distribution network |

The overall period for performance is 60 calendar days from the order to commence, including Stage 1 the desk review, the geophysical acquisition and submission of the targeting reports. The Client's decision period at the decision gate (ten working days) is excluded from that count. The indicative period per borehole, including drilling, development, testing and wellhead securing, is 7 to 9 days.

The Contractor shall be able to move from site to site without interruption; The Contractor shall take account of access conditions at the end of the rainy season (low risk in November, target villages easy to access).

## 11.2 Supervision and staffing

- A geophysicist or hydrogeologist shall lead the survey, carry out the inversion and sign the targeting reports.

- An experienced site foreman shall be present on site at all times during Stage 2; the contact details of the foreman and of the Contractor's technical manager shall be provided before commencement.

- A hydrogeologist or qualified engineer shall supervise the pumping tests and sign the interpretation note.

- A weekly progress meeting shall be held with the project team; a brief one-page progress report shall be submitted each week.

# 12. Supervision, hold points and acceptance

## 12.1 Hold points

The following stages are hold points: the Contractor may not proceed without the written approval or the attendance of the Client's representative.

- Approval of the targeting report and of the target adopted, and the Client's decision at the decision gate, before any mobilisation of the drilling rig (article 3.6).

- Approval of the drilling location and signature of the siting minutes, before drilling.

- Decision to stop drilling and approval of the completion program, before the casing string is run.

- Inspection of casing and screen in the yard, before they are run.

- Witnessing of the placing of the gravel pack and of the annular grouting.

- Witnessing of the end of development (turbidity and sand content).

- Approval of the pumping test protocol and of the rate for the constant-rate test.

## 12.2 Provisional and final acceptance

Provisional acceptance is granted once all the boreholes are complete, the deliverables submitted and any reservations cleared. It is recorded in joint minutes for each site.

Final acceptance takes place at the end of a defects liability period of twelve months from provisional acceptance. During that period the Contractor guarantees the integrity of the borehole — no collapse of the casing, no abnormal silting, no failure of the grouting or of the apron — and shall intervene at its own cost within 15 days on simple notification by the Client, save where the cause is manifestly unconnected with the execution of the works.

# 13. Contractual and financial provisions

## 13.1 Form of prices

The contract is let on unit prices applied to the quantities actually executed and jointly recorded. Prices are firm and not subject to revision for the duration of the contract, expressed in Lao kip (LAK) inclusive of all taxes, and cover all obligations of execution, mobilization, transport, accommodation, taxes and insurance.

Items marked OPTION in the bill of quantities shall be priced but are excluded from the comparison of offers and are ordered only on written instruction. The Contractor shall have no claim in respect of options not exercised or conditional tranches not ordered.

## 13.2 Payment

| Milestone | Share | Condition |
| --- | --- | --- |
| Stage 1 | 100 % of the Stage 1 amount | On submission and acceptance of the orientation notes, the targeting reports and the siting minutes. No advance is paid on Stage 1. Payable whatever the decision taken at the decision gate |
| Advance on Stage 2 | 20 % of the Stage 2 amount ordered | After the order to commence the works, submission of the HSE plan and provision of an advance payment bank guarantee of the same amount |
| Interim payment | 50 % | Pro rata to the boreholes completed, cased, developed, tested and secured, on joint verification |
| Balance | 20 % | After provisional acceptance and submission of all the deliverables of article 10 |
| Retention | 10 % | Released at final acceptance, or replaceable by a performance bank guarantee of the same amount |

## 13.3 Liquidated damages and remedies

- Delay in execution: 0.1 % of the contract amount per calendar day of delay, capped at 10 % of the contract amount.

- Late submission of deliverables: 0.05 % of the contract amount per day, from the contractual date.

- Re-acquisition of geophysical data made necessary by inadequate data quality (RMS above 10 %, excessive proportion of points removed, absence of topographic correction): at the Contractor's sole cost.

- Replacement of an unproductive borehole: at the Contractor's sole cost, with the client’s payment agreed in advance, within the limits of article 6.6.

- Serious breach of the HSE or social provisions (article 9): formal notice, then suspension of the works at the Contractor's cost; on repetition, termination for default.

- Non-compliant materials (casing, screen, gravel): removal and complete replacement at the Contractor's sole cost.

## 13.4 Subcontracting and variations

Subcontracting requires the Client's prior written agreement; the Contractor remains solely responsible for performance. Subcontracting of the geophysical survey is permitted provided the subcontractor, its equipment and its geophysicist are identified in the offer and meet the requirements of article 3.2. Subcontracting does not affect the Contractor's replacement obligation under article 6.6.

Any variation to the technical program, to depths or to locations shall be the subject of a written instruction; no additional work carried out without a written instruction will be paid for.

# 14. Content of offers and evaluation

## 14.1 Composition of the offer

- Administrative documents: company registration in Lao PDR, water well drilling licence, tax certificate, bank details.

- References: list of water wells constructed in Lao PDR over the last three years, with location, depth, yield obtained, client and certificates of satisfactory completion.

- Geophysical references: list of resistivity surveys carried out in Lao PDR, and two anonymized targeting reports submitted as samples, so that the quality of the inversion and of the interpretation can be assessed.

- Plant — drilling: description and photographs of the rig (make, capacity, year), compressor, pumping test equipment (test pump, flow meter or weir, dip meter) and logistical resources. The test pump shall be shown to be capable of at least 12 m³/h at 40 m.

- Plant — geophysics: make and model of the resistivity meter, number of channels and electrodes, cable length available, GPS used.

- Personnel: site organization chart, curriculum vitae of the geophysicist or hydrogeologist responsible for the survey, of the site foreman and of the engineer responsible for the tests.

- Technical method statement: survey methodology (array, spacing, length and orientation of lines, inversion parameters), drilling methodology, typical well design, completion program, development and testing protocol, HSE and sludge management arrangements.

- A statement confirming that the well design offered accepts a 4" pump at 10 m³/h and 60 m head, giving the real inside diameter of the casing offered.

- Provisional program by stage and by site.

- Bill of quantities completed and signed (Annex A), and detailed estimate of quantities.

## 14.2 Evaluation criteria

| Criterion | Weighting | Points considered |
| --- | --- | --- |
| Technical and plant capacity — drilling | 20 pts | Compliance with the minimum characteristics of article 5.1 (pull-up, torque, compressors, test pump), condition and age of the plant, testing equipment owned, ability to run two rigs |
| Geophysical capacity | 15 pts | Number of channels and electrodes, inversion software, experience of the geophysicist, quality of the two sample targeting reports |
| References and experience in Lao PDR | 12 pts | Number and relevance of water supply boreholes constructed, in particular in Bolikhamxay or in comparable alluvial settings |
| Quality of the technical method statement | 10 pts | Soundness of the survey and drilling methods, coherence of the well design, testing protocol |
| HSE, environmental and social arrangements | 8 pts | Sludge management, safety, grievance mechanism, code of conduct |
| Programme and ability to hold the November window | 5 pts | Realism and detail of the programme, sequencing of Stages 1 and 2, availability of resources |
| Financial offer | 30 pts | Marked in inverse proportion to the amount of the lowest compliant evaluated offer, options excluded |
| TOTAL | 100 pts | — |

Offers scoring less than 45 of the 70 technical points will be set aside before the financial offer is opened. The Client reserves the right to visit the Contractor's premises and to contact its references.

Offers shall remain valid for 30 days from the closing date. The Client is not bound to accept the lowest or any offer, and may cancel the consultation without incurring liability.

# Annex A — Bill of quantities

The bill of quantities is deliberately set out at the level of broad categories rather than as a long list of elementary items. The intention is to let each tenderer price the work according to its own methods and its own cost structure, rather than force it into a breakdown that may not match how it actually works.

The tenderer completes the summary table below, and attaches behind it its own detailed breakdown for each category. That breakdown should show the elementary items making up each category, with their quantities and rates — for example, for item 2.3, the metres drilled by diameter and formation, the metres of casing and screen, the volume of gravel pack, the metres of grouting, the hours of development and the cost of site reinstatement.

A more detailed and internally consistent breakdown is credited in the technical evaluation (article 14.2). It allows the Client to check that the specifications of articles 5 and 6 have actually been priced, to verify unit prices against the market, and to negotiate any variation during execution on an agreed basis. A summary table returned without a supporting breakdown will be assessed as weak on that criterion.

Prices are in Lao kip, inclusive of all taxes, and cover all obligations of execution, mobilization, transport, accommodation, taxes and insurance. Items marked OPTION shall be priced but are ordered only on written instructions and are excluded from the comparison of offers. Quantities shown are estimates and do not commit the Client. There is no obligation on the Client to order any borehole: Stage 2 depends on the outcome of Stage 1.

| No. |  | Category |  | Basis | Est. qty |  |  | Rate (LAK) |  | Amount (LAK) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| STAGE 1 — GEOPHYSICAL INVESTIGATION AND SITING (FIRM) |  |  |  |  |  |  |  |  |  |  |
| 1.1 | Desk review of the Client’s documentation and hydrogeological orientation note |  | lump sum |  |  | 1 |  |  |  |  |
| 1.2 | Mobilization and demobilization of the geophysical crew — single lump sum covering the whole campaign, all three villages |  | lump sum |  |  | 1 |  |  |  |  |
| 1.3 | Geophysical investigation of one village: acquisition, processing, inversion and interpretation of at least two ERT lines and one vertical sounding at each retained target, to the requirements of article 3.2 |  | per village |  |  | 3 |  |  |  |  |
| 1.4 | Targeting report, joint site confirmation and siting minutes |  | lump sum |  |  | 1 |  |  |  |  |
| 1.5 | Additional ERT line, on written instruction — OPTION |  | per line |  |  | 3 |  |  |  |  |
| 1.6 | Additional vertical sounding, on written instruction — OPTION |  | per sounding |  |  | 6 |  |  |  |  |
| STAGE 2 — DRILLING WORKS (CONDITIONAL TRANCHE AND OPTION) — SIX BOREHOLES MAXIMUM |  |  |  |  |  |  |  |  |  |  |
| 2.1 | Mobilization and demobilization of the drilling rig — single lump sum covering the whole campaign |  | lump sum |  |  | 1 |  |  |  |  |
| 2.2 | Move of the drilling rig between villages |  | lump sum |  |  | 1 |  |  |  |  |
| 2.3 | Complete borehole at the reference depth of 65 m, all inclusive: site set-up and clearing; surface hole ø ≥ 220 mm and drilling ø ≥ 165 mm in all formations; supply and installation of casing DN ≥ 125 mm and machine-slotted screen; gravel pack, bentonite seal and sanitary annular grouting over some 43 m; development (6 h minimum) and disinfection; verticality check; wellhead securing; lined mud pit, sludge disposal and full site reinstatement; cuttings box and completion report |  | per borehole |  |  | 6 |  |  |  |  |
| 2.4 | Adjustment above or below the 65 m reference depth, applied to the whole equipped borehole (drilling, casing, screen, gravel pack and grouting) |  | per meter |  |  | 90 |  |  |  |  |
| 2.5 | Pumping tests: step-drawdown test, 12 h constant-rate test, 3 h recovery and signed hydrodynamic interpretation |  | per borehole |  |  | 6 |  |  |  |  |
| 2.6 | Plugging and abandonment of a borehole — OPTION |  | per borehole |  |  | 2 |  |  |  |  |
| 2.8 | Campaign synthesis note |  | lump sum |  |  | 1 |  |  |  |  |
| OPTIONAL ITEMS |  |  |  |  |  |  |  |  |  |  |
| 3.1 | Extension of the constant-rate test to 24 h — OPTION |  | per borehole |  |  | 6 |  |  |  |  |
| 3.2 | Physico-chemical and bacteriological laboratory analysis — OPTION |  | per borehole |  |  | 6 |  |  |  |  |
| 3.3 | Reinforced concrete apron 2.00 × 2.00 × 0.15 m with drainage channel — OPTION |  | per borehole |  |  | 6 |  |  |  |  |
| 3.4 | Temporary fence 4 × 4 m and bilingual information board — OPTION |  | per borehole |  |  | 6 |  |  |  |  |
| 3.5 | Downhole camera inspection of the completed borehole — OPTION |  | per borehole |  |  | 6 |  |  |  |  |

# Annex B — Borehole summary sheet template

| Item | Entry |
| --- | --- |
| Borehole identifier |  |
| Village / district / province |  |
| GPS coordinates (WGS 84) and elevation |  |
| Reference of geophysical line and target adopted |  |
| Depth to top of aquifer: predicted (survey) / observed |  |
| Start and completion dates of drilling |  |
| Drilling method and rig used |  |
| Total depth drilled (m) |  |
| Diameters drilled (mm) and intervals |  |
| Casing: material, diameter, wall thickness, plain intervals |  |
| Real inside diameter of casing (mm) |  |
| Screen: type, aperture, intervals |  |
| Gravel pack: grading, intervals |  |
| Bentonite seal and grouting: intervals |  |
| Water strikes: depths and estimated yields |  |
| Static water level (m bgl) and date of measurement |  |
| Development: duration and method |  |
| Turbidity and sand content at end of development |  |
| Critical yield (m³/h) |  |
| Operating yield over 12 h, measured in November (m³/h) |  |
| Corrected yield for design (0.75 × Qm) (m³/h) |  |
| Measured yield of 10 m³/h sustained? (yes / no) |  |
| Dynamic water level at operating yield (m bgl) |  |
| Drawdown and specific capacity (m³/h/m) |  |
| Estimated transmissivity (m²/s) |  |
| Recommended pump setting depth (m) |  |
| Water quality: compliance / failing parameters |  |
| Wellhead securing completed (yes/no, date) |  |
| Observations and operating recommendations |  |

# Annex C — Typical borehole design

The plate that follows has contractual value as a schematic. It fixes the architecture expected of the borehole and the temporary wellhead protection. Depths shown are indicative: they are fixed borehole by borehole by the Client, on the basis of the approved targeting report, and then adjusted in the light of the lithological log recorded and the water strikes encountered (hold point, article 12.1). Materials, minimum thicknesses and the dimensions of the wellhead protection are, by contrast, mandatory.

The dashed pump shown on the plate is for information only: the pump is supplied and installed by the Client and is not part of this contract. It is shown so that the Contractor can verify that the well design accepts it.

## C.1 Summary of mandatory requirements

| Item | Mandatory requirement |
| --- | --- |
| Prior investigation | At least two ERT lines per village, ≥ 48 electrodes, ≥ 350 m, depth of investigation ≥ 80 m, plus a vertical sounding at each retained target; target approved by the Client before drilling |
| Pump duty | 10 m³/h at approx. 60 m total dynamic head; 4" submersible pump supplied and installed by the Client |
| Required sustainable yield | Measured yield ≥ 10 m³/h in November, giving a corrected design yield of ≈ 7.5 m³/h |
| Design depth | Set by the approved targeting report; nominal 65 m (minimum 60 m, maximum paid depth 80 m) |
| Drilled diameter, cased section | ≥ 165 mm (annular space ≥ 40 mm) |
| Inside diameter of casing | ≥ 125 mm real (4" pump, cable and probe) |
| Casing | Food-grade PVC-U, Thai standard, DN 125 mm minimum, wall ≥ 6 mm, threaded joints |
| Screen | Machine-slotted 1.0 mm, open area ≥ 6 %, length ≥ 12 m (18 m preferred); no screen above 45 m |
| Sump | ≥ 3 m, threaded watertight bottom plug |
| Centralisers | Every 6 m, and at the top and bottom of the screen |
| Gravel pack | Washed rounded siliceous gravel 2–3 mm, disinfected at 50 mg/L, from 2 m below the bottom screen to 3 m above the top screen |
| Bentonite seal | ≥ 2 m thick |
| Annular grouting | Continuous from the top of the bentonite seal to ground level (≈ 43 m), tremie-placed bottom-up |
| Pump setting (not in contract) | ≥ 8 m below the corrected dynamic level and ≥ 6 m above the top of the screen |
| Casing stick-up | 0.50 to 0.80 m above finished ground level, cut square |
| Cap | Galvanised steel ≥ 3 mm or cast iron, lockable, removable without cutting. |
| Concrete apron (option) | Reinforced concrete 350 kg/m³, 2.00 × 2.00 × 0.15 m, welded mesh, fall ≥ 2 %, kerb and channel, 7 days wet curing |

## C.2 Typical borehole design

Plate C.2 — Typical borehole design (depths indicative, diameters not to scale)